## Version modification record
Version | Date | Content | Note
V1.0 | 2024-06-14 | First edition（Register address not filled）
V1.1 | 2024-08-30 | Register address filled

## Frame formats
Frame formats
Communication description Communication interface: MODBUS-TCP/IP Communication connection mode: Ethernet connection Communication working mode: half-duplex Communication response time：less-than 100ms Communication timeout：the default timeout period is 30S Communication IP Address：192.168.200.171 Communication Server Port：502
Table 1 Function code list
Function Code | Function
03 | read holding registers(output register)
06 | Preset single register
16 | Preset multiple registers
Table 2 Exception code list
Exception Code | MODBUS name | Comments
03 | Illegal Data Address | Dependant on the request
04 | Illegal Function Code | The function code is unknown by the server
aa | System error | Matching values are not obtained in the system or there is a problem with the program
Table 3 （for Modbus TCP/IP）： MBAP header
Fields | Length | Description |  | Client | Server
Transaction Identifier | 2 Bytes | Indentification of a MODBUS request/response transaction |  | Initialized by the client | Recopied by the server from the received request
Protocol Identifier | 2 Bytes | 0= MODBUS protocol |  | Initialized by the client | Recopied by the server from the received request
Length | 2 Bytes | Number of following Bytes |  | Initialized by the client(request) | Initialized by the server(response)
Unit Identifier | 1 Byte | Identification of a remote slave connected on a serial line or on other buses |  | Initialized by the client | Recopied by the server from the received request
Table 4.1 （for Modbus TCP/IP）： Reading data request
MBAP | Function code（0x03） | Starting Address of register | Quantity of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes
Table 4.2 （for Modbus TCP/IP）： Reading successful response
MBAP | Function code（0x03） | Quantity of Data Bytes | Value of registers
7 Bytes | 1 Byte | 1 Byte | （2*N）Bytes
Table 4.3（for Modbus TCP/IP）： Reading failed response
MBAP | Error Code（0x83） |  | Exeption code（03 or 04 or aa, refer to Table 2）
7 Bytes | 1 Byte |  | 1 Byte
Table 5.1 （for Modbus TCP/IP）： Writing Data request(Writing multiple values)
MBAP | Function Code（0x10） | Starting Address of register | Quantity of registers | Quantity of datas |  | Value of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes | 1 Byte |  | （2*N）Bytes
Table 5.2 （for Modbus TCP/IP）： Writing successful response(Writing multiple values)
MBAP | Function Code（0x10） | Starting Address of register | Quantity of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes
Table 5.3 （for Modbus TCP/IP）： Writing failed response(Writing multiple values)
MBAP | Error Code（0x90） |  | Exeption code（03 or 04 or aa , refer to Table 2）
7 Bytes | 1 Byte |  | 1 Byte
Table 5.1 （for Modbus TCP/IP）： Writing Data request(Writing single value)
MBAP | Function Code（0x06） | Starting Address of register | Value of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes
Table 5.2（for Modbus TCP/IP）： Writing successful response(Writing single value)
MBAP | Function Code | Starting Address of register | Value of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes
Table 5.3 （for Modbus TCP/IP）： Writing failed response(Writing single value)
MBAP | Error Code（0x86） |  | Exeption code（03 or 04 or aa, refer to Table 2）
7 Bytes | 1 Byte |  | 1 Byte

## Point Table Structure
Point Table Structure
Equipment attribution | Point List Category | Equipment type | Number of equipment | Number of registers per device | Register address range (decimal)
Master System | Telemetry, telecommand | Host Summary | 1 | 100 | [0, 99]
| Telemetry, telecommand | meter | 20 | 60 | [100, 1299]
| Telemetry, telecommand | Photovoltaic inverter | 32 | 40 | [1300, 2579]
| Telemetry, telecommand | diesel generator | 5 | 40 | [2580, 2779]
| await a decision | reserve | 1 | 770 | [2780, 3999]
| Telemetry, telecommand | Host Summary | 1 | 200 | [4000, 4199]
| await a decision | reserve | 1 | 800 | [4200, 4999]
From system 1 | Telemetry, telecommand | Slave summary | 1 | 100 | [5000, 5099]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [5100, 5169]
| Telemetry, telecommand | DCDC | 5 | 90 | [5170, 5619]
| Telemetry, telecommand | STS | 1 | 70 | [5620, 5689]
| Telemetry, telecommand | BAMS | 1 | 80 | [5690, 5769]
| Telemetry, telecommand | BCMU | 20 | 60 | [5770, 6969]
| Telemetry, telecommand | air conditioner | 2 | 30 | [6970, 7029]
| Telemetry, telecommand | reserve | 1 | 370 | [7030, 7399]
From system 2 | Telemetry, telecommand | Slave summary | 1 | 100 | [7400, 7499]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [7500, 7569]
| Telemetry, telecommand | DCDC | 5 | 90 | [7570, 8019]
| Telemetry, telecommand | STS | 1 | 70 | [8020, 8089]
| Telemetry, telecommand | BAMS | 1 | 80 | [8090, 8169]
| Telemetry, telecommand | BCMU | 20 | 60 | [8170, 9369]
| Telemetry, telecommand | air conditioner | 2 | 30 | [9370, 9429]
| Telemetry, telecommand | reserve | 1 | 370 | [9430, 9799]
From system 3 | Telemetry, telecommand | Slave summary | 1 | 100 | [9800, 9899]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [9900, 9969]
| Telemetry, telecommand | DCDC | 5 | 90 | [9970, 10419]
| Telemetry, telecommand | STS | 1 | 70 | [10420, 10489]
| Telemetry, telecommand | BAMS | 1 | 80 | [10490, 10569]
| Telemetry, telecommand | BCMU | 20 | 60 | [10570, 11769]
| Telemetry, telecommand | air conditioner | 2 | 30 | [11770, 11829]
| Telemetry, telecommand | reserve | 1 | 370 | [11830, 12199]
From system 4 | Telemetry, telecommand | Slave summary | 1 | 100 | [12200, 12299]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [12300, 12369]
| Telemetry, telecommand | DCDC | 5 | 90 | [12370, 12819]
| Telemetry, telecommand | STS | 1 | 70 | [12820, 12889]
| Telemetry, telecommand | BAMS | 1 | 80 | [12890, 12969]
| Telemetry, telecommand | BCMU | 20 | 60 | [12970, 14169]
| Telemetry, telecommand | air conditioner | 2 | 30 | [14170, 14229]
| Telemetry, telecommand | reserve | 1 | 370 | [14230, 14599]
From system 5 | Telemetry, telecommand | Slave summary | 1 | 100 | [14600, 14699]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [14700, 14769]
| Telemetry, telecommand | DCDC | 5 | 90 | [14770, 15219]
| Telemetry, telecommand | STS | 1 | 70 | [15220, 15289]
| Telemetry, telecommand | BAMS | 1 | 80 | [15290, 15369]
| Telemetry, telecommand | BCMU | 20 | 60 | [15370, 16569]
| Telemetry, telecommand | air conditioner | 2 | 30 | [16570, 16629]
| Telemetry, telecommand | reserve | 1 | 370 | [16630, 16999]
From system 6 | Telemetry, telecommand | Slave summary | 1 | 100 | [17000, 17099]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [17100,17169]
| Telemetry, telecommand | DCDC | 5 | 90 | [17170, 17619]
| Telemetry, telecommand | STS | 1 | 70 | [17620, 17689]
| Telemetry, telecommand | BAMS | 1 | 80 | [17690, 17769]
| Telemetry, telecommand | BCMU | 20 | 60 | [17770, 18969]
| Telemetry, telecommand | air conditioner | 2 | 30 | [18970, 19029]
| Telemetry, telecommand | reserve | 1 | 370 | [19030, 19399]
From system 7 | Telemetry, telecommand | Slave summary | 1 | 100 | [19400, 19499]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [19500, 19569]
| Telemetry, telecommand | DCDC | 5 | 90 | [19570, 20019]
| Telemetry, telecommand | STS | 1 | 70 | [20020, 20089]
| Telemetry, telecommand | BAMS | 1 | 80 | [20090, 20169]
| Telemetry, telecommand | BCMU | 20 | 60 | [20170, 21369]
| Telemetry, telecommand | air conditioner | 2 | 30 | [21370, 21429]
| Telemetry, telecommand | reserve | 1 | 370 | [21430, 21799]
From system 8 | Telemetry, telecommand | Slave summary | 1 | 100 | [21800, 21899]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [21900, 21969]
| Telemetry, telecommand | DCDC | 5 | 90 | [21970, 22419]
| Telemetry, telecommand | STS | 1 | 70 | [22420, 22489]
| Telemetry, telecommand | BAMS | 1 | 80 | [22490, 22569]
| Telemetry, telecommand | BCMU | 20 | 60 | [22570, 23769]
| Telemetry, telecommand | air conditioner | 2 | 30 | [23770, 23829]
| Telemetry, telecommand | reserve | 1 | 370 | [23830, 24199]
From system 9 | Telemetry, telecommand | Slave summary | 1 | 100 | [24200, 24299]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [24300, 24369]
| Telemetry, telecommand | DCDC | 5 | 90 | [24370, 24819]
| Telemetry, telecommand | STS | 1 | 70 | [24820, 24889]
| Telemetry, telecommand | BAMS | 1 | 80 | [24890, 24969]
| Telemetry, telecommand | BCMU | 20 | 60 | [24970, 26169]
| Telemetry, telecommand | air conditioner | 2 | 30 | [26170, 26229]
| Telemetry, telecommand | reserve | 1 | 370 | [26230, 26599]
From system 10 | Telemetry, telecommand | Slave summary | 1 | 100 | [26600, 26699]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [26700, 26769]
| Telemetry, telecommand | DCDC | 5 | 90 | [26770, 27219]
| Telemetry, telecommand | STS | 1 | 70 | [27220, 27289]
| Telemetry, telecommand | BAMS | 1 | 80 | [27290, 27369]
| Telemetry, telecommand | BCMU | 20 | 60 | [27370, 28569]
| Telemetry, telecommand | air conditioner | 2 | 30 | [28570, 28629]
| Telemetry, telecommand | reserve | 1 | 370 | [28630, 28999]
From system 11 | Telemetry, telecommand | Slave summary | 1 | 100 | [29000, 29099]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [29100, 29169]
| Telemetry, telecommand | DCDC | 5 | 90 | [29170, 29619]
| Telemetry, telecommand | STS | 1 | 70 | [29620, 29689]
| Telemetry, telecommand | BAMS | 1 | 80 | [29690, 29769]
| Telemetry, telecommand | BCMU | 20 | 60 | [29770, 30969]
| Telemetry, telecommand | air conditioner | 2 | 30 | [30970, 31029]
| Telemetry, telecommand | reserve | 1 | 370 | [31030, 31399]
From system 12 | Telemetry, telecommand | Slave summary | 1 | 100 | [31400, 31499]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [31500, 31569]
| Telemetry, telecommand | DCDC | 5 | 90 | [31570, 32019]
| Telemetry, telecommand | STS | 1 | 70 | [32020, 32089]
| Telemetry, telecommand | BAMS | 1 | 80 | [32090, 32169]
| Telemetry, telecommand | BCMU | 20 | 60 | [32170, 33369]
| Telemetry, telecommand | air conditioner | 2 | 30 | [33370, 33429]
| Telemetry, telecommand | reserve | 1 | 370 | [33430, 33799]
From system 13 | Telemetry, telecommand | Slave summary | 1 | 100 | [33800, 33899]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [33900, 33969]
| Telemetry, telecommand | DCDC | 5 | 90 | [33970, 34419]
| Telemetry, telecommand | STS | 1 | 70 | [34420, 34489]
| Telemetry, telecommand | BAMS | 1 | 80 | [34490, 34569]
| Telemetry, telecommand | BCMU | 20 | 60 | [34570, 35769]
| Telemetry, telecommand | air conditioner | 2 | 30 | [35770, 35829]
| Telemetry, telecommand | reserve | 1 | 370 | [35830, 36199]
From system 14 | Telemetry, telecommand | Slave summary | 1 | 100 | [36200, 36299]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [36300, 36369]
| Telemetry, telecommand | DCDC | 5 | 90 | [36370, 36819]
| Telemetry, telecommand | STS | 1 | 70 | [36820, 36889]
| Telemetry, telecommand | BAMS | 1 | 80 | [36890, 36969]
| Telemetry, telecommand | BCMU | 20 | 60 | [36970, 38169]
| Telemetry, telecommand | air conditioner | 2 | 30 | [38170, 38229]
| Telemetry, telecommand | reserve | 1 | 370 | [38230, 38599]
From system 15 | Telemetry, telecommand | Slave summary | 1 | 100 | [38600, 38699]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [38700, 38769]
| Telemetry, telecommand | DCDC | 5 | 90 | [38770, 39219]
| Telemetry, telecommand | STS | 1 | 70 | [39220, 39289]
| Telemetry, telecommand | BAMS | 1 | 80 | [39290, 39369]
| Telemetry, telecommand | BCMU | 20 | 60 | [39370, 40569]
| Telemetry, telecommand | air conditioner | 2 | 30 | [40570, 40629]
| Telemetry, telecommand | reserve | 1 | 370 | [40630, 40999]
From system 16 | Telemetry, telecommand | Slave summary | 1 | 100 | [41000, 41099]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [41100, 41169]
| Telemetry, telecommand | DCDC | 5 | 90 | [41170, 41619]
| Telemetry, telecommand | STS | 1 | 70 | [41620, 41689]
| Telemetry, telecommand | BAMS | 1 | 80 | [41690, 41769]
| Telemetry, telecommand | BCMU | 20 | 60 | [41770, 42969]
| Telemetry, telecommand | air conditioner | 2 | 30 | [42970, 43029]
| Telemetry, telecommand | reserve | 1 | 370 | [43030, 43399]
From system 17 | Telemetry, telecommand | Slave summary | 1 | 100 | [43400, 43499]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [43500, 43569]
| Telemetry, telecommand | DCDC | 5 | 90 | [43570, 44019]
| Telemetry, telecommand | STS | 1 | 70 | [44020, 44089]
| Telemetry, telecommand | BAMS | 1 | 80 | [44090, 44169]
| Telemetry, telecommand | BCMU | 20 | 60 | [44170, 45369]
| Telemetry, telecommand | air conditioner | 2 | 30 | [45370, 45429]
| Telemetry, telecommand | reserve | 1 | 370 | [45430, 45799]
From system 18 | Telemetry, telecommand | Slave summary | 1 | 100 | [45800, 45899]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [45900, 45969]
| Telemetry, telecommand | DCDC | 5 | 90 | [45970, 46419]
| Telemetry, telecommand | STS | 1 | 70 | [46420, 46489]
| Telemetry, telecommand | BAMS | 1 | 80 | [46490, 46569]
| Telemetry, telecommand | BCMU | 20 | 60 | [46570, 47769]
| Telemetry, telecommand | air conditioner | 2 | 30 | [47770, 47829]
| Telemetry, telecommand | reserve | 1 | 370 | [47830, 48199]
From system 19 | Telemetry, telecommand | Slave summary | 1 | 100 | [48200, 48299]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [48300, 48369]
| Telemetry, telecommand | DCDC | 5 | 90 | [48370, 48819]
| Telemetry, telecommand | STS | 1 | 70 | [48820, 48889]
| Telemetry, telecommand | BAMS | 1 | 80 | [48890, 48969]
| Telemetry, telecommand | BCMU | 20 | 60 | [48970, 50169]
| Telemetry, telecommand | air conditioner | 2 | 30 | [50170, 50229]
| Telemetry, telecommand | reserve | 1 | 370 | [50230, 50599]
From system 20 | Telemetry, telecommand | Slave summary | 1 | 100 | [50600, 50699]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [50700, 50769]
| Telemetry, telecommand | DCDC | 5 | 90 | [50770, 51219]
| Telemetry, telecommand | STS | 1 | 70 | [51220, 51289]
| Telemetry, telecommand | BAMS | 1 | 80 | [51290, 51369]
| Telemetry, telecommand | BCMU | 20 | 60 | [51370, 52569]
| Telemetry, telecommand | air conditioner | 2 | 30 | [52570, 52629]
| Telemetry, telecommand | reserve | 1 | 370 | [52630, 52999]
From system 21 | Telemetry, telecommand | Slave summary | 1 | 100 | [53000, 53099]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [53100, 53169]
| Telemetry, telecommand | DCDC | 5 | 90 | [53170, 53619]
| Telemetry, telecommand | STS | 1 | 70 | [53620, 53689]
| Telemetry, telecommand | BAMS | 1 | 80 | [53690, 53769]
| Telemetry, telecommand | BCMU | 20 | 60 | [53770, 54969]
| Telemetry, telecommand | air conditioner | 2 | 30 | [54970, 55029]
| Telemetry, telecommand | reserve | 1 | 370 | [55030, 55399]
From system 22 | Telemetry, telecommand | Slave summary | 1 | 100 | [55400, 55499]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [55500, 55569]
| Telemetry, telecommand | DCDC | 5 | 90 | [55570, 56019]
| Telemetry, telecommand | STS | 1 | 70 | [56020, 56089]
| Telemetry, telecommand | BAMS | 1 | 80 | [56090, 56169]
| Telemetry, telecommand | BCMU | 20 | 60 | [56170, 57369]
| Telemetry, telecommand | air conditioner | 2 | 30 | [57370, 57429]
| Telemetry, telecommand | reserve | 1 | 370 | [57430, 57799]
From system 23 | Telemetry, telecommand | Slave summary | 1 | 100 | [57800, 57899]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [57900,57969]
| Telemetry, telecommand | DCDC | 5 | 90 | [57970, 58419]
| Telemetry, telecommand | STS | 1 | 70 | [58420, 58489]
| Telemetry, telecommand | BAMS | 1 | 80 | [58490, 58569]
| Telemetry, telecommand | BCMU | 20 | 60 | [58570,59769]
| Telemetry, telecommand | air conditioner | 2 | 30 | [59770, 59829]
| Telemetry, telecommand | reserve | 1 | 370 | [59830, 60199]
From system 24 | Telemetry, telecommand | Slave summary | 1 | 100 | [60200, 60299]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [60300, 60369]
| Telemetry, telecommand | DCDC | 5 | 90 | [60370, 60819]
| Telemetry, telecommand | STS | 1 | 70 | [60820, 60889]
| Telemetry, telecommand | BAMS | 1 | 80 | [60890, 60969]
| Telemetry, telecommand | BCMU | 20 | 60 | [60970, 62169]
| Telemetry, telecommand | air conditioner | 2 | 30 | [62170, 62229]
| Telemetry, telecommand | reserve | 1 | 370 | [62230, 62599]
From system 25 | Telemetry, telecommand | Slave summary | 1 | 100 | [62600, 62699]
| Telemetry, telecommand | PCS（DCAC） | 1 | 70 | [62700, 62769]
| Telemetry, telecommand | DCDC | 5 | 90 | [62770, 63219]
| Telemetry, telecommand | STS | 1 | 70 | [63220, 63289]
| Telemetry, telecommand | BAMS | 1 | 80 | [63290, 63369]
| Telemetry, telecommand | BCMU | 20 | 60 | [63370, 64569]
| Telemetry, telecommand | air conditioner | 2 | 30 | [64570, 64629]
| Telemetry, telecommand | reserve | 1 | 370 | [64630, 64999]
await a decision | await a decision | reserve | 1 | 536 | [65000, 65535]

## Host Summary
Device | Register address (decimal) | Measurement point name | Register name | Data type | Unit | Note
Host Summary | 0 | operation mode | Work Mode | uint16 |  | 0xAA：On-grid mode 0x55 ：Off-grid mode
| 1 | working state | Work Status | uint16 |  | 1:normal 2:warning 3:fault
| 2 | Total rated power of energy storage | System Total rated power | int32 | 0.1kW | Accumulation of energy storage ratings of added equipment
3
| 4 | Chargeable Capacity of Energy Storage | System Chargeable Energy | uint32 | 0.1kWh | (SOC ceiling - actual SOC)* energy storage rated capacity
5
| 6 | Dischargeable Capacity of Energy Storage | System Dischargeable Energy | uint32 | 0.1kWh | (actual SOC - lower SOC limit)*rated capacity of energy storage
7
| 8 | Charge Power of Energy Storage | System Chargeable Power | uint32 | 0.1kW | Sum of rechargeable power of all energy storage devices
9
| 10 | Discharge Power of Energy Storage | System Dischargeable Power | uint32 | 0.1kW | Sum of dischargeable power of all energy storage devices
11
| 12 | Available Time for Maximum Charge Power | max power charge available time | uint16 | 1min | System rechargeable capacity / Maximum rechargeable power allowance
| 13 | Available Time for Maximum Discharge Power | max power discharge available time | uint16 | 1min | System discharge capacity / Maximum discharge power allowance
| 14 | Actual State of Charge (SOC) of Energy Storage | System SOC | uint16 | 0.1% | average value
| 15 | Reserved | Reserved
| 16 | Reserved | Reserved
| 17 | Reserved | Reserved
| 18 | Reserved | Reserved
| 19 | Active Power of Energy Storage | System Active Power | int32 | 0.1kW | Accumulation of real-time active power from energy storage
20
| 21 | Reactive Power of Energy Storage | System Reactive Power | int32 | 0.1kVar | Accumulation of real-time reactive power for energy storage
22
| 23 | Total Charged Amount of Energy Storage | System Total Charge | uint32 | 10kWh
24
| 25 | Total Discharged Amount of Energy Storage | System Total Discharge | uint32 | 10kWh
26
| 27 | Daily Charged Amount of Energy Storage | System Daily Charge | uint32 | 0.1kWh
28
| 29 | Daily Discharged Amount of Energy Storage | System Daily Discharge | uint32 | 0.1kWh
30
| 31 | Available Reactive Power of Energy Storage | Available reactive power | uint32 | 0.1kVar
32
| 33 | Total Photovoltaic Generation | Total Power Generation | uint32 | 10kWh | logger or the total rounds sent on the meter are accumulated
34
| 35 | Daily Photovoltaic Generation | Daily Power Generation | uint32 | 0.1kWh | The logger or the meter sends an accumulation of daily rounds.
36
| 37 | Installed Capacity of Photovoltaic System | Photovoltaic installed capacity | uint32 | 0.1kWh | Operating Parameter PV Rated Power Setting Value
38
| 39 | Theoretical Active Power of Photovoltaic Systeme | Theoretical active power of photovoltaics | int32 | 0.1kW | All southbound PV equipment rated active cumulative
40
| 41 | Available Active Power of Photovoltaic System | Photovoltaic available active power | uint32 | 0.1kW | Online Southbound PV Equipment Rated Active Accumulation
42
| 43 | Available Reactive Power of Photovoltaic System | Photovoltaic available reactive power | uint32 | 0.1kVar | PV available active power * 0.66
44
| 45 | Active Power of Photovoltaic System | Photovoltaic active power | int32 | 0.1kW | Real-Time Active Accumulation for Southbound Photovoltaic Equipment
46
| 47 | Reactive Power of Photovoltaic System | Photovoltaic reactive power | int32 | 0.1kVar | Real-time reactive power accumulation for southbound photovoltaic equipment
48
| 49 | Total Active Power of Loads on Grid Side | grid side load total power of the meter | int32 | 0.1kW | Load meter data is taken when there is a load meter, and EMS calculated data is reported when there is no load meter.
50
| 51 | Total Active Power of Loads on BACKUP Side | backup side load total power of the meter | int32 | 0.1kW
52
| 53 | Total load power of the system | total load power | int32 | 0.1kW
54
| 55 | Total Battery Power | total battery power | int32 | 0.1kW
56
| 57 | Platform Type | platform | uint16 |  | 1：EMS4.0 2：EMS5.0
| 58 | Protocol Version Number | protocol version number | uint16
| 59 | Dual Power Supply Status | dual power state | uint16 |  | 0：Disconnected state 1：Main power side 2：Backup side
| 60 | System working mode | System mode | uint16 |  | 0：Local_auto_mode 3: Modbus_dp_mode
| 61~99 | reserve | Reserved

## Meter
Device | Register address (decimal) | Measurement point name | Register name | Data type | Unit | Note
grid_gw_meter | 100 | Ua | A phase voltage | int32 | 0.1V
101
| 102 | Ub | B phase voltage | int32 | 0.1V
103
| 104 | Uc | C phase voltage | int32 | 0.1V
105
| 106 | Ia | A phase current | int32 | 0.1A
107
| 108 | Ib | B phase current | int32 | 0.1A
109
| 110 | Ic | C phase current | int32 | 0.1A
111
| 112 | Frequency | Frequency | uint16 | 0.001Hz
| 113 | Total power factor | Total PF | int16 | 0.01PF
| 114 | Pa | A active power | int32 | 0.1kW
115
| 116 | Pb | B active power | int32 | 0.1kW
117
| 118 | Pc | C active power | int32 | 0.1kW
119
| 120 | Sa | A apparent power | int32 | 0.1kVA
121
| 122 | Sb | B apparent power | int32 | 0.1kVA
123
| 124 | Sc | C apparent power | int32 | 0.1kVA
125
| 126 | Total active power | Total active power | int32 | 0.1kW
127
| 128 | Total reactive power | Total reactive power | int32 | 0.1kVar
129
| 130 | Total apparent power | Total apparent power | int32 | 0.1kVA
131
| 132 | Positive active electric energy | Positive active electric energy | uint32 | 0.01kWh | Primary side, energy = Value * 0.01 * CT multiplier * PT multiplier
133
| 134 | Reverse active electric energy | Reverse active electric energy | uint32 | 0.01kWh | Primary side, energy = Value * 0.01 * CT multiplier * PT multiplier
135
| 136 | Current maximum demand of positive active power | The current maximum positive active power demand | uint32 | 0.1kW
137
| 138 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 139 | CT Magnification | ct_ratio | int16
| 140 | PT magnification | pt_ratio | uint16
| 141~159 | reserve | Reserved
dg_meter | 160 | Ua | A phase voltage | int32 | 0.1V
161
| 162 | Ub | B phase voltage | int32 | 0.1V
163
| 164 | Uc | C phase voltage | int32 | 0.1V
165
| 166 | Ia | A phase current | int32 | 0.1A
167
| 168 | Ib | B phase current | int32 | 0.1A
169
| 170 | Ic | C phase current | int32 | 0.1A
171
| 172 | Frequency | Frequency | uint16 | 0.001Hz
| 173 | Total power factor | Total PF | int16 | 0.01PF
| 174 | Pa | A active power | int32 | 0.1kW
175
| 176 | Pb | B active power | int32 | 0.1kW
177
| 178 | Pc | C active power | int32 | 0.1kW
179
| 180 | Sa | A apparent power | int32 | 0.1kVA
181
| 182 | Sb | B apparent power | int32 | 0.1kVA
183
| 184 | Sc | C apparent power | int32 | 0.1kVA
185
| 186 | Total active power | Total active power | int32 | 0.1kW
187
| 188 | Total reactive power | Total reactive power | int32 | 0.1kVar
189
| 190 | Total apparent power | Total apparent power | int32 | 0.1kVA
191
| 192 | Positive active electric energy | Positive active electric energy | uint32 | 0.01kWh | Primary side, energy = Value * 0.01 * CT multiplier * PT multiplier
193
| 194 | Reverse active electric energy | Reverse active electric energy | uint32 | 0.01kWh | Primary side, energy = Value * 0.01 * CT multiplier * PT multiplier
195
| 196 | Current maximum demand of positive active power | The current maximum positive active power demand | uint32 | 0.1kW
197
| 198 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 199 | CT Magnification | ct_ratio | int16
| 200 | PT magnification | pt_ratio | uint16
| 201~219 | reserve | Reserved
pv_gw_meter | 220 | Ua | A phase voltage | int32 | 0.1V
221
| 222 | Ub | B phase voltage | int32 | 0.1V
223
| 224 | Uc | C phase voltage | int32 | 0.1V
225
| 226 | Ia | A phase current | int32 | 0.1A
227
| 228 | Ib | B phase current | int32 | 0.1A
229
| 230 | Ic | C phase current | int32 | 0.1A
231
| 232 | Frequency | Frequency | uint16 | 0.001Hz
| 233 | Total power factor | Total PF | int16 | 0.01PF
| 234 | Pa | A active power | int32 | 0.1kW
235
| 236 | Pb | B active power | int32 | 0.1kW
237
| 238 | Pc | C active power | int32 | 0.1kW
239
| 240 | Sa | A apparent power | int32 | 0.1kVA
241
| 242 | Sb | B apparent power | int32 | 0.1kVA
243
| 244 | Sc | C apparent power | int32 | 0.1kVA
245
| 246 | Total active power | Total active power | int32 | 0.1kW
247
| 248 | Total reactive power | Total reactive power | int32 | 0.1kVar
249
| 250 | Total apparent power | Total apparent power | int32 | 0.1kVA
251
| 252 | Positive active electric energy | Positive active electric energy | uint32 | 0.01kWh | Primary side, energy = Value * 0.01 * CT multiplier * PT multiplier
253
| 254 | Reverse active electric energy | Reverse active electric energy | uint32 | 0.01kWh | Primary side, energy = Value * 0.01 * CT multiplier * PT multiplier
255
| 256 | Current maximum demand of positive active power | The current maximum positive active power demand | uint32 | 0.1kW
257
| 258 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 259 | CT Magnification | ct_ratio | int16
| 260 | PT magnification | pt_ratio | uint16
| 261~279 | reserve | Reserved
other meter | 280~1299 | reserve | Reserved

## PV Inverter
Device | Register address (decimal) | Measurement point name | Register name | Data type | Unit | Note
PV Inverter_n PV inverter No. n ( n∈[1,32] ) | 1300+(n-1)*40 | Active power regulation | Active regulator | uint16 | % | 0%-100%
| 1301+(n-1)*40 | Reserved | Reserved
| 1302+(n-1)*40 | Ua | A Phase voltage | uint16 | 0.1V
| 1303+(n-1)*40 | Ub | B Phase voltage | uint16 | 0.1V
| 1304+(n-1)*40 | Uc | C Phase voltage | uint16 | 0.1V
| 1305+(n-1)*40 | A-phase frequency | Frequency | uint16 | 0.01Hz
| 1306+(n-1)*40 | Reserved | Reserved
| 1307+(n-1)*40 | Reserved | Reserved
| 1308+(n-1)*40 | Power generation of the day | Feed Engery to grid in today | int16 | 0.1kWh
| 1309+(n-1)*40 | Generating power | Feeding power | int16 | 0.1kW
| 1310+(n-1)*40 | Working mode | Work Mode | int16
| 1311+(n-1)*40 | Internal temperature of inverter | Inverter internal temperature | int16 | 0.1℃
| 1312+(n-1)*40 | Total power generation | Total Feed Energy to grid | uint32 | 0.1kWh
1313+(n-1)*40
| 1314+(n-1)*40 | Fault information 1 | Fault information1 | uint32
1315+(n-1)*40
| 1316+(n-1)*40 | Fault information 2 | Fault information2 | uint32
1317+(n-1)*40
| 1318+(n-1)*40 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 1319+(n-1)*40 | Real communication status | real communication status | int16 |  | 1:normal 0:lost
| 1320~1339+(n-1)*40 | reserve | Reserved

## Diesel generator
Device | Register address (decimal) | Measurement point name | Register name | Data type | Unit | Note
Diesel generator_n Diesel generator No. n ( n∈[1,5] ) | 2580+(n-1)*40 | Uab | Line voltage between A to B | uint16 | 0.1V | 0~600.0
| 2581+(n-1)*40 | Ubc | Line voltage between B to C | uint16 | 0.1V | 0~600.0
| 2582+(n-1)*40 | Uca | Line voltage between C to A | uint16 | 0.1V | 0~600.0
| 2583+(n-1)*40 | Frequency | Frequency | uint16 | 0.01Hz | 40.00~70.00
| 2584+(n-1)*40 | Total active power | Total active power | int16 | 0.1kW
| 2585+(n-1)*40 | Total reactive power | Total reactive power | int16 | 0.1kVar
| 2586+(n-1)*40 | Total apparent power | Total apparent power | int16 | 0.1kVA
| 2587+(n-1)*40 | Total power factor | Total PF | int16 | 0.01PF | -1.00~1.00
| 2588+(n-1)*40 | Oil pressure | Oil pressure | int16 | Kpa
| 2589+(n-1)*40 | Coolant temperature | Coolant temperature | int16 | 0.1℃
| 2590+(n-1)*40 | Engine temperature | Engine temperature | int16 | 0.1℃
| 2591+(n-1)*40 | Fuel temperature | Fuel temperature | int16 | 0.1℃
| 2592+(n-1)*40 | Engine speed | Engine speed | uint16 | rpm
| 2593+(n-1)*40 | Generate total energy | Generator KVA hours | uin32 | 0.1kVAh
2594+(n-1)*40
| 2595+(n-1)*40 | Coolant level | Coolant level | int16 | %
| 2596+(n-1)*40 | Fuel level | Fuel level | int16 | %
| 2597+(n-1)*40 | DG fault information 1 | dg fault message | uint32
2598+(n-1)*40
| 2599+(n-1)*40 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 2600~2619+(n-1)*40 | reeserve | Reserved

## Control
Device | Register address (decimal) | Measurement point name | Register name | Data type | Unit | Note
TA telemetry | 4000 | Active power setting | Active power setpoint | int32 | 0.1kW | charge：- discharge：+
4001
| 4002 | Reactive power setting | Reactive power setpoint | int32 | 0.1kVar | leading：- lagging：+
4003
| 4004~4149 | reserve | reserve
TC telecontrol | 4150 | Switching commands | Modle On/Off Command | uint16 |  | 0：mode off 1：mode on
| 4151 | Clear Error Reporting Command | Failure clearance command | uint16 |  | 0：false 1：true
| 4152 | System working mode | System Mode | uint16 |  | 0：Local_auto_mode 3: Modbus_dp_mode
| 4153~4199 | reserve | reserve

## Slave summary
Device | Register address required + (n-1)*2400 (decimal) | Measurement point name | Register name | Data type | Unit | Note
Slave_summary[n] Summary of slave n ( n∈[1,25] ) | 5000 | EMS real-time operating mode | Work Status | uint16 | 0.1kWh | 1:normal 2:warning 3:fault
| 5001 | Rechargeable capacity | System Chargeable Energy | uint32 | 0.1kWh
5002
| 5003 | Discharging capacity | System Dischargeable Energy | uint32 | 0.1kWh
5004
| 5005 | Rechargeable power | System Chargeable Power | uint32 | 0.1kW
5006
| 5007 | Discharging power | System Dischargeable Power | uint32 | 0.1kW
5008
| 5009 | Active power | Active Power | int32 | 0.1kW
5010
| 5011 | Reactive power | Reactive Power | int32 | 0.1kW
5012
| 5013 | Total charge | Total Charge | uint32 | 1kWh
5014
| 5015 | Total discharge | Total Discharge | uint32 | 1kWh
5016
| 5017 | Daily charge | Daily Charge | uint32 | 0.1kWh
5018
| 5019 | Daily discharge | Daily Discharge | uint32 | 0.1kWh
5020
| 5021~5052 | Input Trunk Node Status (DI 1-32) | Dry Node Fault Status | 32*uint16 |  | 0：NA 1：triggered 2：Not triggered
| 5053 | EMS error message 1 | System Fault Status 1 | uint32
5054
| 5055 | EMS error message 2 | System Fault Status 2 | uint32
5056
| 5057 | EMS error message 3 | System Fault Status 3 | uint32
5058
| 5059 | EMS error message 4 | System Fault Status 4 | uint32
5060
| 5061~5099 | resrve | Reserved

## PCS(DCAC)
Device | Register address required + (n-1)*2400 (decimal) | Measurement point name | Register name | Data type | Unit | Note
PCS[n]（DCAC） PCS of slave n ( n∈[1,25] ) | 5100 | DCAC start stop status | DCAC start-stop state | uint16 |  | 0：mode off 1：mode on 2：standby
| 5101 | DCAC fault status | DCAC fault state | uint16 |  | 0：normal 1：fault
| 5102 | Total AC power factor | Total Power Factor | int16 | 0.01PF
| 5103 | AC frequency | Grid Frequency | uint16 | 0.001Hz
| 5104 | ambient temperature | Ambient temperature | Int16 | 0.1℃
| 5105 | AC Uab | AC line voltage A to B | uint16 | 0.1V
| 5106 | AC Ubc | AC line voltage B to C | uint16 | 0.1V
| 5107 | AC Uca | AC line voltage C to A | uint16 | 0.1V
| 5108 | AC Ia | Phase A Current | int16 | 0.1A
| 5109 | AC Ib | Phase B Current | int16 | 0.1A
| 5110 | AC Ic | Phase C Current | int16 | 0.1A
| 5111 | AC Pa | A active power | int16 | 0.1kW
| 5112 | AC Pb | B active power | int16 | 0.1kW
| 5113 | AC Pc | C active power | int16 | 0.1kW
| 5114 | Reserved | Reserved
| 5115 | Grid type (safety) | Grid Type | int16
| 5116 | working mode | Work Mode | uint16 |  | 0: PQ 1: VF 2：VSG
| 5117 | DC voltage | DC Voltage | uint16 | 0.1V
| 5118 | DC current | DC Current | int16 | 0.1A
| 5119 | Total DC power | DC Power | int16 | 0.1kW
| 5120 | active power | Active Power | int16 | 0.1kW
| 5121 | reactive power | Reactive Power | int16 | 0.1kVar
| 5122 | apparent power | Apparent Power | int16 | 0.1kVA
| 5123 | Daily charge on AC side | Daily Charge | uint16 | 0.1kWh
| 5124 | Total charge on AC side | Total Charge | uint32 | 0.1kWh
5125
| 5126 | Daily discharge on AC side | Daily Discharge | uint16 | 0.1kWh
| 5127 | Total discharge on AC side | Total Discharge | uint32 | 0.1kWh
5128
| 5129 | Total DC branch: Total DC side charging capacity | DC String: Accumulative charged energy | uint32 | 0.1kWh
5130
| 5131 | Total DC branch: Total discharge on DC side | DC String: Accumulative discharged | uint32 | 0.1kWh
5132
| 5133 | DCAC fault information 1 | DCAC fault message 1 | uint32
5134
| 5135 | DCAC fault information 2 | DCAC fault message 2 | uint32
5136
| 5137 | DCAC fault information 3 | DCAC fault message 3 | uint32
5138
| 5139 | DCAC fault information 4 | DCAC fault message 4 | uint32
5140
| 5141 | DCAC fault information 5 (Azure) | DCAC fault message 5 | uint32
5142
| 5143 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 5144~5169 | reserve | Reserved

## DCDC
Device | Register address required + (n-1)*2400 (decimal) | Measurement point name | Register name | Data type | Unit | Note
DCDC[n][m]_summary Summarized data for DCDC m of slave n ( n∈[1,25] ，m∈[1,5]） | 5170+(m-1)*90 | Start stop status | start-stop state | uint16 |  | 0：mode off 1：mode on
| 5171+(m-1)*90 | Fault status | fault state | uint16 |  | 0：normal 1：fault 2：warning
| 5172+(m-1)*90 | BUS side (battery): Power | BUS side: power | int16 | 0.1kW
| 5173+(m-1)*90 | BUS side: current | BUS side: voltage | uint16 | 0.1V | 0~1000.0
| 5174+(m-1)*90 | BUS side: current | BUS side: current | int16 | 0.1A | ‐2000.0~2000.0
| 5175+(m-1)*90 | BUS side: cumulative charging power | BUS side: Accumulative charged energy | uint32 | 0.1kWh | 0~2^32
5176+(m-1)*90
| 5177+(m-1)*90 | BUS side: cumulative discharge quantity | BUS side: Accumulative discharged energy | uint32 | 0.1kWh | 0~2^32
5178+(m-1)*90
| 5179+(m-1)*90 | DC side (PV side):Power | DC side: power | int16 | 0.1kW
| 5180+(m-1)*90 | DC side: voltage | DC side: voltage | uint16 | 0.1V | 0~1000.0
| 5181+(m-1)*90 | DC side: current | DC side: current | int16 | 0.1A | ‐2000.0~2000.0
| 5182+(m-1)*90 | DC Side: Total Discharge Capacity | DC side: Accumulative discharged energy | uint32 | 0.1kWh | 0~2^32
5183+(m-1)*90
| 5184+(m-1)*90 | Module temperature | Module temperature | int16 | 0.1℃ | 40.0~120.0
| 5185+(m-1)*90 | Ambient temperature | Ambient temperature | int16 | 0.1℃ | ‐20.0~80.0
| 5186+(m-1)*90 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 5187~5199+(m-1)*90 | reserve | Reserved
DCDC[n][m]_String[N] Nth branch data of the mth DCDC of the nth slave ( n∈[1,25] ，m∈[1,5]， N∈[1,12]） | 5200+(m-1)*90+(N-1)*5 | Branch circuit ${N}: start-stop status | Branch ${N}: start-stop state | uint16 |  | 0：mode off 1：mode on 2：sleep
| 5201+(m-1)*90+(N-1)*5 | Branch ${N}: Fault state | Branch ${N}: Fault state | uint16 |  | 0：normal 1：fault 2：warning
| 5202+(m-1)*90+(N-1)*5 | Branch ${N}: Voltage (BUS side) | Branch ${N}: BUS side voltage | uint16 | 0.1V | 0~1000.0
| 5203+(m-1)*90+(N-1)*5 | Branch ${N}: Power (DC side) | Branch ${N}: DC side power | int16 | 0.1kW
| 5204+(m-1)*90+(N-1)*5 | Branch ${N}: Voltage (DC side) | Branch ${N}: DC side voltage | uint16 | 0.1V | 0~1000.0

## STS
Device | Register address required + (n-1)*2400 (decimal) | Measurement point name | Register name | Data type | Unit | Note
STS[n] STS of the nth slave ( n∈[1,25] ) | 5620 | Uab(grid side) | Line voltage between A to B(Grid) | uint16 | 0.1V | 0~600.0
| 5621 | Ubc(grid side) | Line voltage between B to C(Grid) | uint16 | 0.1V | 0~600.0
| 5622 | Uca(grid side) | Line voltage between C to A(Grid) | uint16 | 0.1V | 0~600.0
| 5623 | Frequency (grid side) | Frequency(Grid) | uint16 | 0.01Hz | 40.00~70.00
| 5624 | Pa (grid side) | A active power(Grid) | int16 | 0.1kW
| 5625 | Pb (grid side) | B active power(Grid) | int16 | 0.1kW
| 5626 | Pc (grid side) | C active power(Grid) | int16 | 0.1kW
| 5627 | Sa (grid side) | A apparent power(Grid) | int16 | 0.1kVA
| 5628 | Sb (grid side) | B apparent power(Grid) | int16 | 0.1kVA
| 5629 | Sc (grid side) | C apparent power(Grid) | int16 | 0.1kVA
| 5630 | Total active power (grid side) | Total active power(Grid) | int16 | 0.1kW
| 5631 | Total reactive power (grid side) | Total reactive power(Grid) | int16 | 0.1kVar
| 5632 | Total apparent power (grid side) | Total apparent power(Grid) | int16 | 0.1kVA
| 5633 | Total power factor (grid side) | Total PF (Grid) | int16 | 0.01PF | -1.00~1.00
| 5634 | Uab(load side) | Line voltage between A to B(Load) | uint16 | 0.1V | 0~600.0
| 5635 | Ubc(load side) | Line voltage between B to C(Load) | uint16 | 0.1V | 0~600.0
| 5636 | Uca(load side) | Line voltage between C to A(Load) | uint16 | 0.1V | 0~600.0
| 5637 | Ia (load side) | A current(Load) | int16 | 0.1A | ‐1500.0~1500.0
| 5638 | Ib (load side) | B current(Load) | int16 | 0.1A | ‐1500.0~1500.0
| 5639 | Ic (load side) | C current(Load) | int16 | 0.1A | ‐1500.0~1500.0
| 5640 | Frequency (load side) | Frequency(Load) | uint16 | 0.01Hz | 40.00~70.00
| 5641 | Pa (load side) | A active power(Load) | int16 | 0.1kW
| 5642 | Pb (load side) | B active power(Load) | int16 | 0.1kW
| 5643 | Pc (load side) | C active power(Load) | int16 | 0.1kW
| 5644 | Qa (load side) | A reactive power(Load) | int16 | 0.1kVar
| 5645 | Qb (load side) | B reactive power(Load) | int16 | 0.1kVar
| 5646 | Qc (load side) | C reactive power(Load) | int16 | 0.1kVar
| 5647 | Sa (load side) | A apparent power(Load) | int16 | 0.1kVA
| 5648 | Sb (load side) | B apparent power(Load) | int16 | 0.1kVA
| 5649 | Sc (load side) | C apparent power(Load) | int16 | 0.1kVA
| 5650 | Total active power (load side) | Total active power(Load) | int16 | 0.1kW
| 5651 | Total reactive power (load side) | Total reactive power(Load) | int16 | 0.1kVar
| 5652 | Total apparent power (load side) | Total apparent power(Load) | int16 | 0.1kVA
| 5653 | Total power factor (load side) | Total PF (Load) | int16 | 0.01PF | -1.00~1.00
| 5654 | STS communication timeout | STS_CommTimeout | uint16 | 1s | 0: Not limited t：t （s）
| 5655 | parallel off-grid state | Grid interconnection mode | int16 |  | 0: Grid-tied 1: Off-grid
| 5656 | working state | work state | int16 |  | 1:normal 2:warning 3:fault
| 5657 | Module Temperature | Module temperature | int16 | 0.1℃ | 40.0~120.0
| 5658 | STS fault message 1 | STS fault message 1 | uint32
5659
| 5660 | STS fault message 2 | STS fault message 2 | uint32
5661
| 5662 | STS fault message 3 | STS fault message 3 | uint32
5663
| 5664 | STS fault message 4 | STS fault message 4 | uint32
5665
| 5666 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 5667~5689 | reserve | Reserved

## BAMS
Device | Register address required + (n-1)*2400 (decimal) | Measurement point name | Register name | Data type | Unit | Note
BAMS[n] Battery stack data of the nth slave ( n∈[1,25] ) | 5690 | voltage | Total Voltage | uint16 | 0.1 V
| 5691 | current | Total Current | int16 | 0.1 A
| 5692 | SOC | SOC | uint16 | 0.1%
| 5693 | SOH | SOH | uint16 | 0.1%
| 5694 | Maximum charge current | Maximum Charge Current | uint16 | 0.1A
| 5695 | Maximum discharge current | Maximum Discharge Current | uint16 | 0.1A
| 5696 | Total Charge | Total Charge energy | uint32 | 0.1kWh
5697
| 5698 | Total Discharge | Total Discharge energy | uint32 | 0.1kWh
5699
| 5700 | Charge/discharge cycles | Number Of Battery Cycle | uint16
| 5701 | Insulation impedance | Insulated resistance | uint16 | 1kΩ
| 5702 | Allowable charging flag bit | Allow charging flag | uint16
| 5703 | Allowable discharge flag bit | Allow discharging flag | uint16
| 5704 | Apply for charging flag bit | apply charging flag | uint16
| 5705 | soc need calibration flag | soc need calibration flag | uint16
| 5706 | actual power | Actual Power | int16 | 0.1kW
| 5707 | Maximum Cell Voltage | Maximum Cell Voltage | int16 | 0.001V
| 5708 | Maximum cell voltage RACK position | Maximum Cell Voltage Position（#RACK） | uint16
| 5709 | Maximum cell voltage PACK position | Maximum Cell Voltage Position（#PACK） | uint16
| 5710 | Maximum cell voltage CELL position | Maximum Cell Voltage Position（#CELL） | uint16
| 5711 | Minimum Cell Voltage | Minimum Cell Voltage | int16 | 0.001V
| 5712 | Minimum cell voltage RACK position | Maximum Cell Voltage Position（#RACK） | uint16
| 5713 | Minimum cell voltage PACK position | Maximum Cell Voltage Position（#PACK） | uint16
| 5714 | Minimum cell voltage CELL position | Maximum Cell Voltage Position（#CELL） | uint16
| 5715 | Maximum cell temperature | Maximum Cell Temperature | int16 | 0.1℃
| 5716 | Maximum cell temperature RACK position | Maximum Cell Temperature Position（#RACK) | uint16
| 5717 | Maximum cell temperature PACK position | Maximum Cell Temperature Position（#PACK) | uint16
| 5718 | Maximum core temperature measurement point location | Maximum Cell Temperature Position（#POINT) | uint16
| 5719 | Minimum Cell Temperature | Minimum Cell Temperature | int16 | 0.1℃
| 5720 | Minimum cell temperature RACK position | Minimum Cell Temperature Position（#RACK) | uint16
| 5721 | Minimum cell temperature PACK position | Minimum Cell Temperature Position（#PACK) | uint16
| 5722 | Minimum core temperature measurement point location | Minimum Cell Temperature Position（#POINT) | uint16
| 5723 | Maximum pole temperature | Maximum pole temperature | int16 | 0.1℃
| 5724 | Main Relay Status | main_relay_status | uint32 |  | bit_n：Representing the main relay status of cluster n+1，n∈[0~31]. 0：open；1：close
5725
| 5726 | Reserved | Reserved
| 5727 | Communication status | communication status | uint16 |  | 1:normal 0:lost
| 5728 | BMS fault information 1 | bms_fault1 | uint32
5729
| 5730 | BMS fault information 2 | bms_fault2 | uint32
5731
| 5732 | BMS fault information 3 | bms_fault3 | uint32
5733
| 5734 | BMS fault information 4 | bms_fault4 | uint32
5735
| 5736 | bms_fault5(Class I/II/III alarms) | bms_fault5 | uint32
5737
| 5738 | bms_fault6(Class I/II/III alarms) | bms_fault6 | uint32
5739
| 5740 | bms_fault7(Class I/II/III alarms) | bms_fault7 | uint32
5741
| 5742 | bms_fault8(Class I/II/III alarms) | bms_fault8 | uint32
5743
| 5744~5769 | reserve | Reserved

## BCMU
Device | Register address required + (n-1)*2400 (decimal) | Measurement point name | Register name | Data type | Unit | Note
BCMU[n][m] Cluster m of data from slave no. n ( n∈[1,25] ，m∈[1,20]） | 5770+(m-1)*60 | voltage | Voltage | uint16 | 0.1 V
| 5771+(m-1)*60 | current | Current | int16 | 0.1 A
| 5772+(m-1)*60 | SOC | SOC | uint16 | 0.1%
| 5773+(m-1)*60 | SOH | SOH | uint16 | 0.1%
| 5774+(m-1)*60 | Insulation impedance | Insulated resistance | uint16 | 1kΩ
| 5775+(m-1)*60 | Maximum Cell Voltage | Maximum Cell Voltage | int16 | 0.001V
| 5776+(m-1)*60 | Maximum cell voltage PACK position | Maximum Cell Voltage Position（#PACK） | uint16
| 5777+(m-1)*60 | Maximum cell voltage CELL position | Maximum Cell Voltage Position（#CELL） | uint16
| 5778+(m-1)*60 | Minimum Cell Voltage | Minimum Cell Voltage | int16 | 0.001V
| 5779+(m-1)*60 | Minimum cell voltage PACK position | Minimum Cell Voltage Position（#PACK） | uint16
| 5780+(m-1)*60 | Minimum cell voltage CELL position | Minimum Cell Voltage Position（#CELL） | uint16
| 5781+(m-1)*60 | Maximum cell temperature | Maximum Cell Temperature | int16 | 0.1℃
| 5782+(m-1)*60 | Maximum cell temperature PACK position | Maximum Cell Temperature Position（#PACK） | uint16
| 5783+(m-1)*60 | Maximum core temperature measurement point location | Maximum Cell Temperature Position（#POINT） | uint16
| 5784+(m-1)*60 | Minimum Cell Temperature | Minimum Cell Temperature | int16 | 0.1℃
| 5785+(m-1)*60 | Minimum cell temperature PACK position | Minimum Cell Temperature Position（#PACK） | uint16
| 5786+(m-1)*60 | Minimum core temperature measurement point location | Minimum Cell Temperature Position（#POINT） | uint16
| 5787+(m-1)*60 | Main relay status | Main relay status | uint16 |  | 0：open；1：close
| 5788+(m-1)*60 | Precharge relay status | Precharged relay status | uint16 |  | 0：open；1：close
| 5789+(m-1)*60 | Negative relay status | Negative relay status | uint16 |  | 0：open；1：close
| 5790+(m-1)*60 | Molded case circuit breaker status | Molded case circuit breaker status | int16 |  | 0：open；1：close
| 5791+(m-1)*60 | Cluster fault information 1 | bmu_fault1 | uint32
5792+(m-1)*60
| 5793+(m-1)*60 | Cluster fault information 2 | bmu_fault2 | uint32
5794+(m-1)*60
| 5795+(m-1)*60 | Cluster fault information 3 | bmu_fault3 | uint32
5796+(m-1)*60
| 5797+(m-1)*60 | Cluster fault information 4 | bmu_fault4 | uint32
5798+(m-1)*60
| 5799+(m-1)*60 | bmu_fault5(Class I/II/III alarms) | bmu_fault5 | uint32
5800+(m-1)*60
| 5801+(m-1)*60 | bmu_fault6(Class I/II/III alarms) | bmu_fault5 | uint32
5802+(m-1)*60
| 5803+(m-1)*60 | bmu_fault7(Class I/II/III alarms) | bmu_fault5 | uint32
5804+(m-1)*60
| 5805+(m-1)*60 | bmu_fault8(Class I/II/III alarms) | bmu_fault5 | uint32
5806+(m-1)*60
| 5807+(m-1)*60 | Communication status | communication status | uint16 |  | 1:normal 0:lost
| 5808~5829+(m-1)*60 | reserve | Reserved

## Air conditioner
Device | Register address required + (n-1)*2400 (decimal) | Measurement point name | Register name | Data type | Unit | Note | 备注
Air_conditioner[n][m] Air conditioner data No. m for slave No. n ( n∈[1,25] ，m∈[1,2]） | 6970+(m-1)*30 | Equipment working status | Working condition of equipment | int16 |  | 1:Standby 2:Run 3:Fault | 1:Standby: guiding air conditioner does not support
| 6971+(m-1)*30 | Reserved | Reserved
| 6972+(m-1)*30 | Cabinet return air temperature (room temperature) | Cabinet return air temperature (indoor temperature) | int16 | 0.1℃
| 6973+(m-1)*30 | Cabinet return air humidity (room humidity) | Air return humidity inside the cabinet (indoor humidity) | int16 | 0.1%
| 6974+(m-1)*30 | Condenser temperature | Condenser temperature | int16 | 0.1℃
| 6975+(m-1)*30 | Evaporator temperature (exhaust temperature) | Evaporator temperature (exhaust temperature) | int16 | 0.1℃
| 6976+(m-1)*30 | Refrigeration stop point (Refrigeration opening point = Refrigeration stop point + Refrigeration return difference) | Refrigeration stopping point | int16 | 0.1℃ | 7~50
| 6977+(m-1)*30 | Refrigeration return difference | Refrigeration return difference | int16 | 0.1℃ | 1~15
| 6978+(m-1)*30 | Heating stop point (Heating On Point = Heating Off Point - Heating Return Difference) | Heating stop point | int16 | 0.1℃ | -40~20
| 6979+(m-1)*30 | Heating return difference | Heating return difference | uint16 | 0.1℃ | 1~15
| 6980+(m-1)*30 | Air conditioning fault information 1 | Air conditioning warning information 1 | uint32
6981+(m-1)*30
| 6982+(m-1)*30 | Air conditioning fault information 2 | Air conditioning warning information 2 | uint32
6983+(m-1)*30
| 6984+(m-1)*30 | Communication status | communication status | int16 |  | 1:normal 0:lost
| 6985~6999+(m-1)*30 | reserve | Reserved